SPECIFICATION SECTION XXX

PRODUCT: COMMERCIAL REVERSE OSMOSIS SYSTEM

1.0 GENERAL	Furnish a commercial reverse osmosis system (RO) as specified here in this section and as called for in the equipment schedule for the reduction of total dissolved solids. The RO shall be supplied complete, and assembled entirely by one manufacturer. The system shall include all components required for proper operation. These components include system control package, flow meters, high pressure pump, membranes, pre-filter, adjustment valves, pressure gauges, automatic inlet valve, and frame. The RO shall be a Watts Pure Water brand model number PWR8024____ manufactured by Watts.

2.0 RELATED SECTIONS	XXX

3.0 COMPONENTS

3.1 System Support Frame

All components of the reverse osmosis (RO) system will be mounted on a single support frame. The support frame shall be constructed of welded carbon steel with an exterior powder coat finish. The frame will consist of: the frame base constructed of 2.5” X 2.5” square tubing with a ¼”wall thickness and 2 ½” structural angle iron, a membrane housing rack constructed of 2 ½” and 2” structural angle iron, and a 16 gauge 24” high X 42” long metal panel for mounting instrumentation, gauges, and controls. Two mounting plates will be welded on to the top surface of the frame base. One mounting plate will be ½” thick to provide the mounting surface for the pre filter. The other mounting plate will be ¾” thick to provide the mounting surface for the pump.

3.2 Pre Filter

The pre-filter shall be a 316 stainless steel multi round vertical type filter housing with replaceable filter elements. The exterior of the housing will have a poly coat film for superior corrosion resistance. To reduce the accumulation of water on the RO support frame the filtration vessel shall mount to the support frame with heavy duty stainless steel legs. The filter housing shall be sized for 196 gallons per minute at a 3 psi drop using 5 micron pleated cartridges. The replaceable filter elements shall be a pleated type five micron nominally rated cartridge with plastisol end caps. The pleated filter fabric shall be composed of 100% polyester to resist the growth of microbiologic films.

3.3 High Pressure Pump

A high pressure pump will be provided, mounted on the RO frame, to boost the membrane feed water pressure to a maximum of 250 psi. The pump shall be a vertical multi-stage type. Connecting flanges/couplings, impellers, intermediate housing, and pump housing shall be constructed of 304 or 316 stainless steel. All motors must be 230/460 volt 3 phase with TEFC motor housing. The horsepower requirements for 40, 60, 80 and 100 gallon per minute (gpm) production systems shall be 15, 20, 25, and 30 horsepower respectively.

3.4 Membrane and Membrane Housings

The membrane housings shall be constructed of filament wound epoxy FRP, for superior corrosion resistance, with thermoplastic end plates. The maximum operating pressure of the housings shall be 300 psi at 120 deg. F (48 deg. C) with an 1800 psi rated burst pressure. Cleaning ports must be arranged within the housing array so that the system can be cleaned by each membrane stage. The housing feed water, wastewater, and cleaning ports shall be constructed of 316 stainless steel. Membranes shall be thin film composite high rejection 8”X40” Toray brand model TM720-370. Membranes must have a minimum average salt rejection of 99% under the standard test conditions of 225 psi feed pressure and 77 deg. F (25 deg. C), with a 2000 ppm NaCl feed solution at a pH of 7.0.

3.5 System Controls

The system will include electronic and hydraulic controls for automatic operation and manual adjustment. The electronic controller shall be a micro processor based controller with inputs for system status and outputs for automation of the RO components. Input signals shall be: low feed water pressure, feed water conductivity, permeate water conductivity, pretreatment interlock, and tank full shutdown. Output signals shall be: open/close automatic inlet valve, start/stop high-pressure pump, low percent ionic rejection alarm, automatic fast flush, high permeate conductivity divert to drain, and high conductivity alarm. The controller will have a backlit LCD screen to display operating data, including percent ionic rejection, and separate LED indicators for specific alarm and operation status. The controller must be able to operate at temperatures between 32 deg. F (0 deg. C) minimum to 140 deg. F (60 deg. C) maximum. Manual hydraulic control valves will be provided on the RO system to regulate pump discharge volume, reject recycle volume, and reject water volume. The valves shall be globe valves, constructed of 316 stainless steel, and rated for 300 psi maximum working pressure.

3.6 Flow indicators and Gauges

The RO system will be supplied with pressure gauges to indicate the pressure of the pre-filter inlet, pre-filter outlet, pump discharge, membrane feed water, and reject water. All pressure gauges shall be glycerin filled, 304 stainless steel cased, with an acrylic window. Flow meters will be provided to give an indication of product, reject, and recycle water flow rates. Flow meter flow rate scales are to be calibrated to gallons per minute and liters per minute within 3 percent accuracy. Flow meters shall be variable area inline type with union connectors at each end to ease internal cleaning of the meter body. Meter bodies are to be constructed of polysulfone, with 316 stainless steel float and float rod, and viton orings. All pressure gauges and flow meters are to be mounted next to the electronic controller so that all are in plain view of the operator while the system is running.

3.7 System Piping

Pump discharge piping, high pressure membrane feed water piping, and interconnecting membrane feed water piping shall be 316 stainless steel schedule 40. Pump suction and permeate water piping will be schedule 80 PVC.

3.8 Test Kit

Provide a Myron L model 6 P hand held water quality meter along with pH 4 and pH 10 calibration solutions and conductivity KCl- 7000 (7 mS), 442-3000 TDS calibration solutions. Each calibration solution shall be provided in a one quart quantity. Also provide a silt density index test kit, Watts model number T3031, for testing RO feed water SDI.

4.0 SERVICES

4.1 Warranty

Provide a 1 year parts and labor warranty for the system to protect against manufacturers defects. System shall not be subjected to water temperatures above 100 deg. F (37 deg. C), below 35 deg. F (2 deg. C), iron, hardness, or chlorine.

4.2 Start Up

The Contractor providing the equipment shall provide start up of the RO System, a complete set of operating, maintenance, and installation instructions, one complete set of spare pre-filter cartridges for the pre-filter housing, and operator training.