SPECIFICATION SECTION XXX

PRODUCT: COMMERCIAL REVERSE OSMOSIS SYSTEM

1.0 GENERAL	Furnish a commercial reverse osmosis system (RO) as specified here in this section and as called for in the equipment schedule for the reduction of total dissolved solids. The RO shall be supplied complete, and assembled entirely by one manufacturer. System to include all components required for proper operation of the system. These components include system control package, flow meters, high pressure pump, membranes, pre-filter, adjustment valves, pressure gauges, automatic inlet valve, and frame.  The RO shall be a Watts Pure Water brand model number PWR4011____ manufactured by Watts.

2.0 RELATED SECTIONS	XXX

3.0 COMPONENTS

3.1 System Support Frame

All components of the reverse osmosis (RO) system will be mounted on a single support frame. The support frame shall be constructed of a one piece broke 304 stainless steel panel measuring .10” in thickness. The support frame shall be suitable for wall mounting.

3.2 Pre Filter

The pre-filter housing shall be a single element type constructed of FDA grade reinforced polypropylene and certified to NSF/ANSI standard 42. The housing will have a 100 PSI maximum working pressure and a maximum temperature rating of 100 deg. F (37 deg. C). The housing will have 1” NPT inlet and outlet and accept a 4 ½” X 10” single replaceable filter cartridge element.. The housing will be sized to flow 15 GPM at a pressure drop of 3 PSI using a five micron pleated cartridge. The replaceable filter element shall be a pleated type five micron nominally rated cartridge with plastisol end caps. The pleated filter fabric shall be composed of 100% polyester to resist the growth of microbiologic films.

3.3 High Pressure Pump

A high pressure pump will be provided, mounted on the RO frame, to boost the membrane feed water pressure to a maximum of 250 psi. The pump shall be a multi-stage type with 304 stainless steel pump housing, motor adaptor base, pump shaft, and discharge. Impellers shall be constructed of acetal. All motors must be 230 volt 1 phase with ODP motor housings. 1.25 and 2.5 gpm production systems will use a 1 horsepower motor and 3.75 gpm production systems will use a 1.5 horsepower motor to ensure adequate membrane feed water volume and pressure.

3.4 Membrane and Membrane Housings

The membrane housings shall be constructed of fiberglass reinforced plastic for superior corrosion resistance, with glass reinforced polypropylene end caps. The maximum operating pressure of the housings shall be 300 psi. The housing’s maximum operating temperature will be 100 deg. F (37 deg. C). Membranes shall be Watts brand low energy thin film composite 4”X40” model W-4040-LE. Membranes must have a minimum average salt rejection of 95% under the standard test conditions of 225 psi feed pressure, and 77 deg. F (25 deg. C), with a 2000 ppm Na Cl feed solution at a pH of 7.0.

3.5 System Controls

The system will include electronic and hydraulic controls for automatic operation and manual adjustment. The electronic controller shall be a micro processor based controller with inputs and outputs for automation of the RO components.  Input signals shall be: low feed water pressure, tank level full, and pretreatment interlock. Output signals shall be: open/close automatic inlet valve and start/stop high-pressure pump. The controller shall have an adjustable 10 minute through 80 minute delayed automatic restart after a low feed water pressure shut down to prevent on off cycling of the system during a low feed water pressure condition. The controller will have a rocker switch for manual on off control of the system and indicator lights for tank full/ pretreatment interlock, low pressure shut down, and supply power. The electronic controls will be housed in an ABS electrical enclosure with a NEMA 3 rated gasket sealed access door. The automatic inlet valve will be a normally closed nylon globe valve rated for 150 PSI maximum working pressure, 176 deg. F (80 deg. C) maximum temperature, with a 24V coil. Manual hydraulic control valves will be provided on the RO system to regulate reject recycle and reject water volume. The reject water and recycle water adjustment valves shall be globe valves, constructed of 316 stainless steel, and rated for 300 psi maximum working pressure.

3.6 Flow indicators and Gauges

The RO system will be supplied with pressure gauges to indicate the pressure of the pre-filter inlet, pre-filter outlet, and pump discharge water. All pressure gauges shall have an acrylic window. The pump discharge pressure gauge will be glycerine filled. Flow meters will be provided to give an indication of product and reject water flow rates. Flow meter flow rate scales are to be calibrated to gallons per minute and liters per minute within 3 percent accuracy. Flow meters shall be variable area inline type with disconnects at each end to ease internal cleaning of the meter body. Meter bodies are to be constructed of polysulfone or acrylic, with 316 stainless steel float and float rod, and viton orings. Prefilter inlet/outlet and pump discharge pressure gauges and all flow meters are to be mounted next to the electronic controller so that all are in plain view of the operator while the system is running.

3.7 System Piping

Pump suction, pump discharge, reject and reject recycle piping will be 300 psi stainless steel and high pressure hose. Membrane interconnecting piping will be close coupled 316 stainless steel with victaulic clamps. Permeate piping will be polyethylene tubing.

3.8 Test Kit

Provide a Myron L model 6 P hand held water quality meter along with pH 4 and pH 10 calibration solutions and conductivity KCl- 7000 (7 mS), 442-3000 TDS calibration solutions. Each calibration solution shall be provided in a one quart quantity. Also provide a silt density index test kit, Watts model number T3031, for testing RO feed water SDI.

4.0 SERVICES

4.1 Warranty

Provide a 1 year parts and labor warranty for the system to protect against manufacturers defects. System shall not be subjected to water temperatures above 100 deg. F (37 deg. C), below 35 deg. F (2 deg. C), iron, hardness, or chlorine.

4.2 Start Up

The Contractor providing the equipment shall provide start up of the RO system, a complete set of operating, maintenance, and installation instructions, one complete set of spare pre-filter cartridges for the pre-filter housing, and operator training.